## Slide 1: Measurements of the wind turbine induction zone
21th meeting of the Power Curve Working Group
Frederik Ettrup Brink and Nicolai Gayle Nygaard
13 December 2016, Glasgow, Scotland

## Slide 2: Introduction
8 offshore wind farms in Northern Europe
Traditional power curve verifications show close match to manufacturers power curve
Induction zone measured with nacelle based lidar
Very low turbulence

## Slide 3: Wind Iris measurement setup

## Slide 4: Data filtering
Turbine
  Not stopped
  Not starting/stopping
  Not curtailed
Lidar
  RWS0availability and RWS1availability above 0.6
  Valid data at >3 ranges
  Not in wake

## Slide 5: Model of the upstream induction zone
Vortex sheet theory:

## Slide 6: Fit induction model to average wind speed at each range

## Slide 7: Fit induction model to every single 10 min dataset

## Slide 8: Similar blockage effects for the flat part of the Ct-curve

## Slide 9: Turbine platform differences

## Slide 10: Comparison of measurement campaigns

## Slide 11: AEP issue #1: Measured power curve at different ranges and at

## Slide 12: AEP issue #2: Filtering away the real conditions
  Low turbulence and in some cases also high shear have a negative impact on the performance

## Slide 13: Conclusion
The induction zone has been studied from a number of power performance tests at DONG Energy’s offshore wind farms
The vortex sheet induction model provides a good fit to the data and is used in this study to estimate the upstream free wind speed
At wind speeds below rated power the estimated free stream is found to be about 1.0% higher compared to the wind speed at 2.5D
‘Off-design’ low turbulence site conditions at offshore wind farms have a negative impact on performance

## Slide 14: Fitting the induction model to data
, where is the rotor diameter, is the measurement ranges and is the corresponding wind speeds
Define
Simply solve for model parameters and using polyfit:
        %% MATlab example
        p = polyfit(xhat_vec, u_vec, 1);
        a = - p(1)/p(2);
        uinf = p(2);